## Slide 1
ES 1500V 10.0 SERIES
1. Hole size of mounting panel.
ES 1000V/1500V
8.0 SERIES
ES 1000V 6.0 SERIES
RECEPTACLE CONNECTOR
RECEPTACLE CONNECTOR
3.Socket classification:
INNER SCREW
OUTER SCREW
COPPER BUS
THREAD HOLE
COPPER BUS
THROUGH HOLE
CRIMPING
ES series | Size ΦA | Size ΦB | Size C | Size D | Size E | Size F
ES 1000V 6.0 | 7.5 | 6.5 | 10 | M6*1.0 | M6*1.0 | M6*1.0
ES 1000V 8.0 | 10.6 | 8.5 | 12 | M8*1.25 | M8*1.25 | M8*1.25
ES 1500V 8.0 | 10.6 | 8.5 | 12 | M8*1.25 | M8*1.25 | M8*1.25
ES 1500V 10.0 | 12.6 | 8.3 | 13.3 | M10*1.5 | M10*1.5 | M10*1.5
Key dimensions of sockets:
IES series | Connector P/N | Cable spec | Cable Strip L(mm) | Tool width W(mm) | Crimp height A(mm) | Pull-out force(N)
ES 1000V 6.0 | A082-2M06-C025B-XX-XX | 25mm² | 12±1 | 8.0 | 7.4±0.1 | ≥1900N
 | A082-2M06-C025F-XX-XX | 25mm² | 12±1 | 8.0 | 7.4±0.1 | ≥1900N
ES 1000V 8.0 | A081-2M08-C050B-XX-XX | 50mm² | 18±1 | 12.0 | 10.4±0.1 | ≥2800N
 | A081-2M08-C050F-XX-XX | 50mm² | 18±1 | 12.0 | 10.4±0.1 | ≥2800N
ES 1500V 8.0 | A083-2M08-C050B-XX-XX | 50mm² | 16±1 | 12.0 | 10.4±0.1 | ≥2800N
 | A083-2M08-C050F-XX-XX | 50mm² | 16±1 | 12.0 | 10.4±0.1 | ≥2800N
ES 1500V 10.0 | A083-2M10-C070B-XX-XX | 70mm² | 18±1 | 12.0 | 12.4±0.1 | ≥3500N
 | A083-2M10-C070F-XX-XX | 70mm² | 18±1 | 12.0 | 12.4±0.1 | ≥3500N
4. Crimping socket processing size reference:
PLUG CONNECTOR
1.Cut Cable off outer jacket:
2. Mount connector fittings on both ends in turn :
Cable Nut
Cable seal
Insulation bushing
3. Connector crimping:
The measurement
diagram
The measurement
diagram
CONNECTOR ASSEMBLY
IES series | Connector P/N | Cable spec | Cable OD (mm) | Cable Strip L(mm) | Tool width W(mm) | Crimp height A(mm) | Pull-out force(N)
ES 1000V 6.0 | A082-1F06-C010N-XX-XX | 10mm² | 6.4±0.3 | 12±1 | 8.0 | 6.2±0.1 | ≥900N
 | A082-1F06-C016N-XX-XX | 16mm² | 10.2±0.3 | 12±1 | 8.0 | 7.0±0.1 | ≥1500N
 | A082-1F06-C025N-XX-XX | 25mm² | 10.0±0.3 | 12±1 | 8.0 | 7.4±0.1 | ≥1900N
ES 1000V 8.0 | A081-1F08-C025N-XX-XX | 25mm² | 10.0±0.3 | 18±1 | 12.0 | 7.4±0.1 | ≥1900N
 | A081-1F08-C035N-XX-XX | 35mm² | 11.0±0.4 | 18±1 | 12.0 | 8.8±0.1 | ≥2300N
 | A081-1F08-C050N-XX-XX | 50mm² | 13.0±0.5 | 18±1 | 12.0 | 10.4±0.1 | ≥2800N
ES 1500V 8.0 | A083-1F08-C025N-XX-XX | 25mm² | 10.0±0.3 | 16±1 | 12.0 | 7.4±0.1 | ≥1900N
 | A083-1F08-C035N-XX-XX | 35mm² | 11.0±0.4 | 16±1 | 12.0 | 8.8±0.1 | ≥2300N
 | A083-1F08-C050N-XX-XX | 50mm² | 13.0±0.5 | 16±1 | 12.0 | 10.4±0.1 | ≥2800N
ES 1500V 10.0 | A083-1F10-C035N-XX-XX | 35mm² | 11.0±0.4 | 19±1 | 15.0 | 8.8±0.1 | ≥2300N
 | A083-1F10-C050N-XX-XX | 50mm² | 13.0±0.5 | 19±1 | 15.0 | 10.4±0.1 | ≥2800N
 | A083-1F10-C070N-XX-XX | 70mm² | 15.0±0.5 | 19±1 | 15.0 | 12.4±0.1 | ≥3500N
5.Plug assembly data sheet:
4.Connector Mating
Push
Click
Assembly OK
Pull out
Press button
Pull out
HISTORIES AND REVISIONS
Battery Pin connector
The plug connector can only be used with the corresponding series of sockets, and the device plug can only be used indoors.
WARNING:Risk of burns
The connector heats up during operation.It can heat up to 125℃,depending on the ambient conditions. In this case, the user is responsible for attaching warnings(e.g.,in accordance with DIN EN ISO 13732-1).
1.Safety notes
Only electrically qualified personnel may install and operate the product.
Do not disconnect the connectors under load.
Always connect only “+” to “+”and “-” -“”.
2.Suitable conductor
-Multi-wire flexible copper conductor,class 6 in accordance with IEC 60228
-Outer diameter 6.4 to 15.0mm
Select the appropriate seal for your diameter.
2. Receptacle Assembly :
The socket is assembled on the mounting panel with M4 standard screws and the torque is 0.7 N * m